KINGDOM OF SAUDI ARABIA

MINISTRY OF HIGHER EDUCATION

KING ABDULAZIZ UNIVERSITY

Office of the Vice Presidency

Post-Graduate Studies & Academic Research

Scientific Research Council

Vice President For Graduate Studies & Academic Research

Deanship of Graduate Studies

وكالة الجامعة

للدراسات العليا والبحث العلمي

مجلس البحث العلمي

www.kaau.edu.sa/src

Final Report

Name of College: FACULTY OF ENGINEERING

Name of Department: THERMAL ENG. DESALINATION TEC.

Title: Title of Research: ICE STORAGE SYSTEM FOR THE AIR-CONDITIONING PLANT OF AL-HARAM HOLY MOSQUE

Final Report for Project No.: ( 108 / 424 )

Duration of the project for which the report is written : 9 months

Names of the Investigator (s) :

- Principal Investigator: Dr. M. Badr A. Habeebullah

- Co-Investigator: Prof. Galal M. Zaki

- Co-Investigator:

- Co-Investigator:

Date of Submission of this report : 10 / 01 /1426 H

KINGDOM OF SAUDI ARABIA

MINISTRY OF HIGHER EDUCATION

KING ABDULAZIZ UNIVERSITY

Office of the Vice Presidency

Post-Graduate Studies & Academic Research

Scientific Research Council

وكالة الجامعة

للدراسات العليا والبحث العلمي

مجلس البحث العلمي

1. Title of Project: ICE-STORAGE SYSTEM FOR THE AIR-CONDITIONING PLANT OF AL-HARAM HOLY MOSQUE

2. Principle Investigator: Dr Badr A. Habeebullah

3. Name of the College: Engineering

4. Name of the Department: Thermal Engineering and Desalination Technology

Summary This study is motivated by the special energy situation in the Kingdom of Saudi Arabia, where the energy consumed for air conditioning presents nearly between 60-70% of the generated power. This condition puts angst on the future plans of the energy sector, which is seriously in consideration. Different programs for energy conservation have been launched and many are in adequate progress. Recently the use of cold storage tanks has been introduced and few of the large buildings in Riyadh have already integrated the technology with A/C plants. The importance of the energy storage technology has been demonstrated. Examples of buildings (in the Kingdom and abroad) that use chilled water or ice storage systems are cited. Comprehensive literature review showed that the successful use of energy storage systems depends mainly on the A/C load variation and the time rate of electricity. The governing equations for the process of ice build up on a coil have been developed in a general form, where two phase flow analysis was adopted. Therefore, the mathematical model can simply be used for the cases of direct and indirect energy storage analysis. It is suggested here to build ice storage facility in modular fashion, which makes design and construction a simple routine. 1000 TR storage capacity was selected; the coils (12.5 mm copper pipes) of 700 m length were designed to produce 37 tons of ice per hour. Sensitivity analysis showed that over loading the storage tanks reduces the mass of ice. The total mass of ice decreases with the presence of refrigerants superheat inside the coils. The performance of the ice tanks was investigated and showed that the hourly ice rate is nearly 30% below the ideal mass. This point should be taken into consideration in sizing out storage systems. Cost of ice storage tanks was related to the storage capacity in SR/kWh. The cooling load variation of the A/C units of the Holy Mosque at Mekkah is considered. The plant has 32 chillers of 420 TR capacity each. The load curve for an ordinary day (not in Ramadan or during Hajj) showed a peak of 5290 TR and an average of 4065 TR. Installing an ice storage system has been examined for two different scenarios. Partial storing where 11448 TRh is to be stored in 4 hours that costs about 1.38 million SR. This high cost offsets the feasibility of the storing at present. For a new tariff as 0.06 SR/ kWh and 0.26 SR/kWh during peak periods the cost benefit is marginal during 10 years pay back period after which the daily saving reaches 1718 SR. A full load storage scenario was also examined, which showed a saving of 14843 SR/d after the same payback period. The full load is an attractive approach even if the tariff reached the break even point of 0.0776 SR/kWh. A demonstration test unit that comprises an ice making coil of 75 m long and Glycol cooling loop, operating at -11oC was constructed in the laboratories of the Thermal Engineering Department and ready for future extension of the present work. .

KINGDOM OF SAUDI ARABIA

MINISTRY OF HIGHER EDUCATION

KING ABDULAZIZ UNIVERSITY

Office of the Vice Presidency

Post-Graduate Studies & Academic Research

Scientific Research Council

وكالة الجامعة

للدراسات العليا والبحث العلمي

مجلس البحث العلمي

ملخص التقرير النهائي (عربي)

1-عنوان البحث: خزان طاقة ثلجي لمحطة تكييف الهواء بالحرم المكي الشريف

2-الباحث الرئيسي: د. بدر أحمد حبيب الله

3-أسم الكلية: الهندسة

4-أسم القسم:الهندسة الحرارية وتقنية التحلية

الملخص استُنبطت هذه الدراسة من واقع استهلاك الطاقة الهائل والمتزايد في المملكة العربية السعودية، حيث يُستهلك ما بين 60-70 % من الطاقة الكهربائية المولدة في مجال التكييف. مما وضع هذا الاستهلاك الهائل الكثير من القلق والتفكير الجدي على الخطط المستقبلية لقطاع الطاقة. وقد تم تطوير العديد من الطرق للحفاظ على ترشيد الطاقة الكثير منها في مراحل متقدمة الآن. وحديثا استخدام أنظمة التخزين الثلجي في تكنولوجيا تكييف الهواء بالعديد من المباني الكبيرة في مدينة الرياض وفي أماكن أخرى من المملكة ناهيك عن استخدامها الكبير في دول العالم الأخرى سواء كانت على هيئة التخزين الثلجي أو الماء المبرد مما يعكس أهمية هذه التكنولوجيا والجدوى الاقتصادية من استخدامها في مجال تكييف الهواء. تم استباط وتطوير جميع المعادلات الرياضية المتعلقة بعملية تكوين الثلج على ملف قد بشكل عام حيث تم تبني التحليل الطوري الثنائي مما يجعل عملية التحليل سلسة في حالات تكوين الثلج بصورة مباشرة والتي يستخدم فيها وسيط التبريدبصورة مباشرة أو غير مباشرة اوالتي يستخدم فيها وسيط تبريد ثانوي مثل الجلايكول. وقد تم اقتراح نظام تخزين طاقة ثلجي مبسط، حيث تم اختيار سعة تخزينيه تقدر بحوالي 1000 طن تبريد ويتكون من أنبوب نحاسي بقطر 12.5 ملم وبطول 700 متر للحصول على 37 طن من الثلج بالساعة ومن خلال دراسة أداء خزان الثلج لوحظ أنه في حالة وجود تحميص في الملف فأن ذلك يؤدي إلى نقصان في كتلة الثلج المتكونة و أن معدل تكوين الثلج أقل بحوالي 30% من المعدل المثالي (النظري) مما يدل على ضرورة أخذ هذه النسبة في الاعتبار عند تقدير حجم الخزان الثلجية وذلك لأن تكلفة خزانات تخزين الثلج تعتمد على سعة التخزين وتقيم بـالريال لكل كيلووات ساعة. يتكون التكييف المركزي في الحرم المكي الشريف من 32 مبرد مياه ذي سعة تبريدية قصوى 420 طن تبريد بالساعة لكل منها و أوضح مخطط الحمل ليوم واحد أقصى حمل قد يصل إلى 5290 طن تبريد بالساعة والمعدل 4065 طن تبريد بالساعة. لقد تم تحليل اقتراح استخدام نظام تخزين ثلجي لاحتمالين مختلفين: الاحتمال الأول، التخزين الجزئي وذلك لتخزين 11448 طن تبريد خلال 4 ساعات والذي بينت الدراسة تكلفته بحوالي 1.38مليون ريال والذي هو مبلغ غير مجدي للتخزين حاليا. أما لو كانت التعريفة 0.06ريال لكل كيلو وات ساعة في الأوقات العادية و0.26 ريال لكل كيلو وات ساعة أثناء فترات الذروة فإن فائدة التكلفة هامشية أثناء الـ 10 سنة الأولى وذلك لتسديد تكلفة الخزان الثلجي ، أما الفترة التي تليها فيصل الادخار اليومي إلى 1718 ريال سعودي. أما الاحتمال الثاني وهو تخزين كمية كاملة من الثلج فأنة يؤدي ادخار14843 ريال سعودي باليوم بعد فترة تسديد التكلفة الأولية. يتضح من أن الاحتمال الثاني ذو جدوى اقتصادية حتى إذا وصلت التعريفة إلى نقطة المساواة بين التكلفة والعائد والتي هي 0.0776 ريال سعودي لكل كيلو وات ساعة .لقد تم بناء وحدة اختبار تشمل على ملف لعمل الثلج بطول 75 متر و جلايكول الايثيلين الذي تم تبريده إلى oC 11-في معامل قسم الهندسة الحرارية و جاهز للامتداد المستقبلي للدراسة الحالية.